## Slide 1
Mid-West Electric Consumers Association
Annual Meeting
Claire Vigesaa – Executive Director
ND Transmission Authority
December 13, 2023
Grid Reliability and Transmission

## Slide 2: North Dakota Transmission Authority
Statutory Authority 17-05 North Dakota Century Code
Created by North Dakota Legislature – 2005
Authority – comprised of the three members of the ND Industrial Commission
Governor – Attorney General – Ag Commissioner
Broad Authority
Grants or loans
Issue up to $800 in revenue bonds
Enter lease-sale contracts
Own, lease, rent, dispose of transmission facilities
Enter contracts to construct, maintain or operative transmission facilities
Investigate, plan, prioritize and propose transmission cooridors
Participate in regional transmission organizations

## Slide 3: Topics…
Factors that impact grid reliability
Areas of transmission congestion in ND
What increased transmission capacity means for ND’s “all of the above strategy”
Transmission projects approved for ND
Projects under consideration for ND
Recent Generation Adequacy Studies in ND

## Slide 4
Factors Impact Grid Reliability
Electric Generation Adequacy
Maintenance & Operations of the Grid
Natural Disasters
Man-made Disasters – Physical Security
Cyber Security
Energy Policy!

## Slide 5
Areas of Congestion in North Dakota
The Bakken
Southeast ND

## Slide 6
What Increased Transmission Capacity Means for ND
North Dakota…rich in energy resources
North Dakota is a major energy consumer
Transmission Lines…like Interstate Highways
Power can flow both directions
Provides path to market
Improves system reliability/resilience

## Slide 7
SPP Approved Transmission Projects for ND
345kV Roundup to Kummer Ridge – 35 miles - 2025
345kV Leland Olds to Tioga – 175 miles - 2026
230kV Wheelock-SK 50 miles - 2027
230kV Tande-SK 60 miles - 2027
Statcom – New Town

## Slide 8
MISO Approved Otter Tail Power – MDU JETx Project

## Slide 9
Joint Targeted Interconnection Queue
Recipient of $464 million
DOE GRIP Grant
October 2023
Costs have increased dramatically over this estimate

## Slide 10
HVDC Modernization Project - MN Power Allete
Waiting on MN decision from DOC EERA
ND…working on ND route permit and corridor certificate…submitting early 2024
$50 million DOE
Grant Recipient
October 2023
Construction
2028-2031
Increase capacity from 550MW to 900MW…1,500MW

## Slide 11: North Plains Connector
Linking Together the US Grid
Increasing ND’s Export Capacity

## Slide 12: North Plains Connector - Overview
Route:
  Length: 400 miles
Rating:
  HVDC (VSC), 525kV, 3,000MW
Transmission Interconnections:
  WECC – 3,000MW into Colstrip, MT 500kV system
  MISO – 1,500MW (AC) to Center, ND Substation
  SPP – 1,500MW (AC) to new substation near St. Anthony, ND
Expected in service date: 2030-2031
Project Configuration
Overview Map
  Project’s route is under active development and is subject to change.
Notes: Brant

## Slide 13
NERC Summer 2023 Reliability Risk
Many alerts this summer!

## Slide 14
SPP Alert Trend

## Slide 15
NERC Winter 2023-2024 Reliability Risk Map

## Slide 17
2012 – 2022 On National Peak Generation Comparison
Installed wind nameplate went from 56 to 149 GW in past 10 years, yet capacity at peak load only increased 14 GW representing 3.1% of total resource capacity today

## Slide 19
That’s 0.5%!!

## Slide 20
40 hrs below 200MW
10 hrs actually negative

## Slide 21
Objectives: Model Resource Adequacy and Cost in
MISO and SPP Under Two Scenarios
Step 1: Develop Reasonable Accreditation Values for Wind and Solar
  2018-2022 hourly dataset
    Peak load availability.
    Net peak load availability.
Step 2: Reference Scenario
  EIA planned additions and retirements by 2035.
  Replace with modeled wind solar and four-hour storage.
  Peak load and net load.
Step 3: Ozone Transport Rule (OTR) and Coal Combustion Residual (CCR) Scenario
  Loss of coal and gas by 2035.
  Replace with natural gas, wind, solar, and four-hour storage.
  Peak load and net load.

## Slide 22
Methodology- Developing a Standardized Capacity Accreditation for Renewable Resources
  Peak Load: The hours with the highest electricity demand.
  Net peak load: Gross demand minus wind and solar generation, which allows us to assess the highest demand hours where wind and solar output is the lowest. This is the standard new wind and solar resources should be judged by going forward.
Assess wind and solar variability during peak load and net peak load hours
Chart: Hourly Electricity Generation in SPP to Demonstrate Peak and Net Peak Load

## Slide 23
Even With No EPA impact
MISO Relying Upon Weather & Imports for Reserve
Chart: UCAP
| 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
Coal | 45694.6312 | 45694.6312 | 42713.9212 | 39738.7013 | 38122.3013 | 33464.9813 | 33464.9813 | 32909.3213 | 30178.3612 | 29850.3112 | 29850.3112 | 29850.3112 | 29850.3112 | 29850.3112 | 29850.3112
Gas | 72447.12 | 72447.12 | 74675.25 | 74385.18 | 75329.1 | 74812.68 | 74594.349 | 74594.349 | 75444.849 | 74920.869 | 74920.869 | 74920.869 | 74920.869 | 74920.869 | 74920.869
Petroleum | 3778.8671 | 3778.8671 | 3778.8671 | 3410.1371 | 3410.1371 | 3362.3471 | 3359.1071 | 3359.1071 | 3359.1071 | 3359.1071 | 3359.1071 | 3359.1071 | 3359.1071 | 3359.1071 | 3359.1071
Hydro | 6899.7441 | 6899.7441 | 6899.7441 | 6864.7618 | 6862.3834 | 6860.2032 | 6860.2032 | 6837.212 | 6837.212 | 6837.212 | 6837.212 | 6837.212 | 6837.212 | 6837.212 | 6837.212
Nuclear | 12374.34 | 12374.34 | 12374.34 | 12374.34 | 12374.34 | 12374.34 | 12374.34 | 12374.34 | 12374.34 | 12374.34 | 12374.34 | 12374.34 | 12374.34 | 12374.34 | 12374.34
Biomass | 1128.2407 | 1128.2407 | 1125.3607 | 1098.0007 | 1098.0007 | 1098.0007 | 1098.0007 | 1054.8007 | 1054.8007 | 1054.8007 | 1054.8007 | 1054.8007 | 1054.8007 | 1054.8007 | 1054.8007
LMR | 7875 | 7875 | 7875 | 7875 | 7875 | 7875 | 7875 | 7875 | 7875 | 7875 | 7875 | 7875 | 7875 | 7875 | 7875
Imports | 3638 | 3638 | 3638 | 3638 | 3638 | 3638 | 3638 | 3638 | 3638 | 3638 | 3638 | 3638 | 3638 | 3638 | 3638
Wind | 1757.6101 | 1774.045 | 2346.8397 | 2992.894 | 3388.6126 | 4358.815 | 4644.6807 | 4751.1479 | 5220.3084 | 5366.6814 | 5402.9193 | 5439.1573 | 5475.3952 | 5511.6331 | 5547.8711
Solar | 239.2077 | 239.2077 | 2056.8511 | 4315.5092 | 5658.7855 | 8796.9741 | 9702.2154 | 10039.3614 | 11525.0364 | 11988.5509 | 12103.3043 | 12218.0578 | 12332.8113 | 12447.5647 | 12562.3182
Peak Demand | 116600 | 116600 | 118943.66 | 120133.0966 | 121334.4276 | 122547.7718 | 123773.2496 | 125010.9821 | 126261.0919 | 127523.7028 | 128798.9398 | 130086.9292 | 131387.7985 | 132701.6765 | 134028.6933
Reserve Margin | 137471.4 | 137471.4 | 140234.5751 | 141636.9209 | 143053.2901 | 144483.823 | 145928.6612 | 147387.9478 | 148861.8273 | 150350.4456 | 151853.9501 | 153372.4896 | 154906.2144 | 156455.2766 | 158019.8294
Year | Reserve Margin
2022 | 34%
2023 | 32%
2024 | 30%
2025 | 30%
2026 | 28%
2027 | 27%
2028 | 26%
2029 | 25%
2030 | 23%
2031 | 22%
2032 | 21%
2033 | 20%
2034 | 19%
2035 | 18%
Estimated firm capacity using net peak load capacity accreditation values for wind (5.8%) and solar (12%), 95% for nuclear, and 90% for other thermal generators. Different than MISO cleared UCAP (unforced [accredited] capacity).

## Slide 24
MISO OTR + CCR Scenario: Capacity Shortfall Risk
Chart: UCAP
| 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
Coal | 45694.6312 | 45694.6312 | 42713.9212 | 39183.0413 | 29662.6613 | 26856.4613 | 23276.5313 | 20787.9413 | 15977.8013 | 15977.8013 | 15977.8013 | 15977.8013 | 15977.8013 | 15977.8013 | 15977.8013
Gas | 72447.12 | 72447.12 | 74675.25 | 74385.18 | 75329.1 | 74812.68 | 70268.049 | 70268.049 | 71118.549 | 70594.569 | 70594.569 | 70594.569 | 70594.569 | 70594.569 | 70594.569
Petroleum | 3778.8671 | 3778.8671 | 3778.8671 | 3410.1371 | 3410.1371 | 3362.3471 | 3359.1071 | 3359.1071 | 3359.1071 | 3359.1071 | 3359.1071 | 3359.1071 | 3359.1071 | 3359.1071 | 3359.1071
Hydro | 6899.7441 | 6899.7441 | 6899.7441 | 6864.7618 | 6862.3834 | 6860.2032 | 6860.2032 | 6837.212 | 6837.212 | 6837.212 | 6837.212 | 6837.212 | 6837.212 | 6837.212 | 6837.212
Nuclear | 12374.34 | 12374.34 | 12374.34 | 12374.34 | 12374.34 | 12374.34 | 12374.34 | 12374.34 | 12374.34 | 12374.34 | 12374.34 | 12374.34 | 12374.34 | 12374.34 | 12374.34
Biomass | 1128.2407 | 1128.2407 | 1125.3607 | 1098.0007 | 1098.0007 | 1098.0007 | 1098.0007 | 1054.8007 | 1054.8007 | 1054.8007 | 1054.8007 | 1054.8007 | 1054.8007 | 1054.8007 | 1054.8007
Imports | 3638 | 3638 | 3638 | 3638 | 3638 | 3638 | 3638 | 3638 | 3638 | 3638 | 3638 | 3638 | 3638 | 3638 | 3638
Wind | 1757.6101 | 1774.045 | 2432.3895 | 3288.1857 | 5308.4912 | 6061.2007 | 7958.6953 | 8464.814 | 9418.5221 | 9522.4118 | 9601.0465 | 9679.6813 | 9758.316 | 9836.9507 | 9915.5855
Solar | 239.2077 | 239.2077 | 2327.7589 | 5250.5996 | 11738.4009 | 14187.862 | 20196.595 | 21799.3043 | 24819.3798 | 25148.3638 | 25397.3738 | 25646.3838 | 25895.3938 | 26144.4038 | 26393.4138
Peak Demand | 116600 | 116600 | 118943.66 | 120133.0966 | 121334.4276 | 122547.7718 | 123773.2496 | 125010.9821 | 126261.0919 | 127523.7028 | 128798.9398 | 130086.9292 | 131387.7985 | 132701.6765 | 134028.6933
Reserve Margin | 130592 | 130592 | 133216.8992 | 134549.0682 | 135894.5589 | 137253.5045 | 138626.0395 | 140012.2999 | 141412.4229 | 142826.5471 | 144254.8126 | 145697.3607 | 147154.3343 | 148625.8777 | 150112.1365
Year | Reserve Margin
2022 | 34%
2023 | 33%
2024 | 31%
2025 | 30%
2026 | 28%
2027 | 27%
2028 | 25%
2029 | 24%
2030 | 23%
2031 | 22%
2032 | 21%
2033 | 20%
2034 | 19%
2035 | 18%
Estimated firm capacity using net peak load capacity accreditation values for wind (5.8%) and solar (12%), 95% for nuclear, and 90% for other thermal generators. Different than MISO cleared UCAP (unforced [accredited] capacity). Under this scenario, MISO would be dependent on intermittent resources to meet peak load.

## Slide 25
Even With No EPA impact, SPP Relying Upon
Weather & Imports for Reserve at SPP
Chart: Capacity (MW)
| 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
Coal | 22540.0018 | 22540.0018 | 21905.8712 | 21905.8712 | 20955.9946 | 20955.9946 | 20955.9946 | 19974.4554 | 19974.4554 | 19974.4554 | 19974.4554 | 19974.4554 | 19974.4554 | 19974.4554 | 19974.4554
Gas | 29869.1656 | 29905.7316 | 30546.4111 | 31100.4916 | 31771.5172 | 32361.1284 | 32109.3489 | 32015.2629 | 32015.2629 | 31810.2779 | 31605.293 | 31605.293 | 31605.293 | 31400.308 | 31186.6267
Petroleum | 1670.5498 | 1670.5498 | 1670.5498 | 1670.5498 | 1670.5498 | 1670.5498 | 1642.8298 | 1642.8298 | 1642.8298 | 1642.8298 | 1642.8298 | 1642.8298 | 1642.8298 | 1642.8298 | 1632.9298
Hydro | 3490.001 | 3490.001 | 3490.001 | 3490.001 | 3490.001 | 3490.001 | 3490.001 | 3490.001 | 3490.001 | 3490.001 | 3490.001 | 3490.001 | 3490.001 | 3490.001 | 3490.001
Nuclear | 1949 | 1949 | 1949 | 1949 | 1949 | 1949 | 1949 | 1949 | 1949 | 1949 | 1949 | 1949 | 1949 | 1949 | 1949
Biomass | 189.8352 | 189.8352 | 189.8352 | 189.8352 | 189.8352 | 189.8352 | 189.8352 | 189.8352 | 189.8352 | 189.8352 | 189.8352 | 189.8352 | 189.8352 | 189.8352 | 189.8352
Imports | 876 | 876 | 876 | 876 | 876 | 876 | 876 | 876 | 876 | 876 | 876 | 876 | 876 | 876 | 876
Wind | 2563.2842 | 2563.2842 | 2809.1673 | 2840.4148 | 3216.1816 | 3280.4392 | 3353.7251 | 3625.1478 | 3625.1478 | 3679.7811 | 3734.4144 | 3734.4144 | 3734.4144 | 3789.0478 | 3848.2063
Solar | 64.5879 | 90.7177 | 885.1995 | 988.2442 | 2418.1597 | 2675.1902 | 2968.3338 | 4054.0247 | 4054.0247 | 4272.558 | 4491.0913 | 4491.0913 | 4491.0913 | 4709.6245 | 4946.2586
Peak Demand | 53042 | 53042 | 53492.857 | 53947.5463 | 54406.1004 | 54868.5523 | 55334.935 | 55805.2819 | 56279.6268 | 56758.0036 | 57240.4467 | 57726.9905 | 58217.6699 | 58712.5201 | 59211.5765
Reserve Margin | 60998.3 | 60998.3 | 61516.7855 | 62039.6782 | 62567.0155 | 63098.8351 | 63635.1752 | 64176.0742 | 64721.5708 | 65271.7042 | 65826.5137 | 66386.039 | 66950.3204 | 67519.3981 | 68093.313
Year | Reserve Margin
2022 | 19%
2023 | 20%
2024 | 21%
2025 | 22%
2026 | 23%
2027 | 22%
2028 | 22%
2029 | 20%
2030 | 20%
2031 | 19%
2032 | 18%
2033 | 17%
2034 | 16%
2035 | 15%
Estimated firm capacity using net peak load capacity accreditation values for wind (7.5%) and solar (20.4%), 92% for nuclear, 88% for coal, 83% for natural gas, and 90% for other thermal generators.

## Slide 26
OTR & CCR SPP Scenario: Capacity Shortfall Risk
Chart: UCAP (MW)
| 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
Coal | 22540.0018 | 22540.0018 | 21905.8712 | 20148.5995 | 19198.7229 | 15459.0235 | 10964.7 | 7284.8077 | 3134.3747 | 3134.3747 | 3134.3747 | 3134.3747 | 3134.3747 | 3134.3747 | 3134.3747
Gas | 29869.1656 | 29905.7316 | 30546.4111 | 31100.4916 | 31771.5172 | 32361.1284 | 28491.675 | 28397.589 | 28397.589 | 28397.589 | 28397.589 | 28397.589 | 28397.589 | 28397.589 | 28183.9077
Petroleum | 1670.5498 | 1670.5498 | 1670.5498 | 1670.5498 | 1670.5498 | 1670.5498 | 1642.8298 | 1642.8298 | 1642.8298 | 1642.8298 | 1642.8298 | 1642.8298 | 1642.8298 | 1642.8298 | 1632.9298
Hydro | 3490.001 | 3490.001 | 3490.001 | 3490.001 | 3490.001 | 3490.001 | 3490.001 | 3490.001 | 3490.001 | 3490.001 | 3490.001 | 3490.001 | 3490.001 | 3490.001 | 3490.001
Nuclear | 1949 | 1949 | 1949 | 1949 | 1949 | 1949 | 1949 | 1949 | 1949 | 1949 | 1949 | 1949 | 1949 | 1949 | 1949
Biomass | 189.8352 | 189.8352 | 189.8352 | 189.8352 | 189.8352 | 189.8352 | 189.8352 | 189.8352 | 189.8352 | 189.8352 | 189.8352 | 189.8352 | 189.8352 | 189.8352 | 189.8352
Imports | 876 | 876 | 876 | 876 | 876 | 876 | 876 | 876 | 876 | 876 | 876 | 876 | 876 | 876 | 876
Wind | 2563.2842 | 2563.2842 | 2778.8835 | 3172.6212 | 3488.2043 | 4320.1418 | 6116.5599 | 6903.5412 | 7767.6898 | 7767.6898 | 7767.6898 | 7767.6898 | 7767.6898 | 7767.6898 | 7816.7662
Solar | 64.5879 | 90.7177 | 764.0645 | 2317.0701 | 3506.2506 | 6834.0007 | 14019.6732 | 17167.5984 | 20624.1926 | 20624.1926 | 20624.1926 | 20624.1926 | 20624.1926 | 20624.1926 | 20820.4984
Peak Demand | 53042 | 53042 | 53492.857 | 53947.5463 | 54406.1004 | 54868.5523 | 55334.935 | 55805.2819 | 56279.6268 | 56758.0036 | 57240.4467 | 57726.9905 | 58217.6699 | 58712.5201 | 59211.5765
Reserve Margin | 60998.3 | 60998.3 | 61516.7855 | 62039.6782 | 62567.0155 | 63098.8351 | 63635.1752 | 64176.0742 | 64721.5708 | 65271.7042 | 65826.5137 | 66386.039 | 66950.3204 | 67519.3981 | 68093.313
Year | Reserve Margin
2022 | 19%
2023 | 20%
2024 | 20%
2025 | 21%
2026 | 22%
2027 | 21%
2028 | 20%
2029 | 19%
2030 | 18%
2031 | 18%
2032 | 17%
2033 | 16%
2034 | 16%
2035 | 15%
Estimated firm capacity using net peak load capacity accreditation values for wind (7.5%) and solar (20.4%), 92% for nuclear, 88% for coal, 83% for natural gas, and 90% for other thermal generators. Under this scenario, SPP is dependent on intermittent resources to meet peak load by 2026.

## Slide 27
EPA’s Modeled Grid Only Meets EPA’s Reserve Margin With Generous Wind and Solar Capacity Accreditation and LMR/Import Assumptions
Chart: MISO Current Grid vs. EPA Projected with EPA’s Capacity Accreditation Assumptions
| MISO 2021 | EPA 2028 | EPA 2030 | EPA 2035 | EPA 2040 | EPA 2045 | EPA 2050 | EPA 2055
Coal | 45.695 | 21.6146 | 10.9248 | 0.0536 | 0.0536 | 0.0536 | 0.0152 | 0.0152
Coal Retrofit | 0.10395 | 4.2104 | 4.2144 | 2.1249 | 0 | 0 | 0
Natural Gas | 72.448 | 73.0936 | 77.5371 | 81.8328 | 87.7498 | 102.0184 | 119.1219 | 131.108
NG Retrofit | 1.5563 | 0 | 0 | 0 | 0 | 0 | 0
Nuclear | 12.374 | 11.6005 | 9.7877 | 9.7877 | 6.0313 | 2.8578 | 0.9845 | 0
LMR | 7.875 | 7.875 | 7.875 | 7.875 | 7.875 | 7.875 | 7.875 | 7.875
Imports/Other | 11.353 | 16.8991 | 16.3249 | 15.2249 | 15.2121 | 15.2121 | 14.1271 | 14.1271
Hydro | 4.26 | 3.7405 | 4.2253 | 5.9571 | 6.2707 | 6.2707 | 6.2707 | 6.2707
Wind | 1.758 | 8.1187 | 12.2632 | 16.3594 | 18.1056 | 19.2846 | 19.8147 | 20.0942
Solar | 0.239 | 3.2737 | 9.1795 | 22.525 | 24.1814 | 25.274 | 26.8241 | 28.0329
Battery Storage | 0 | 6.5165 | 7.4809 | 8.1207 | 8.2409 | 9.8899 | 10.7085 | 10.7085
Projected Peak Load | 124.2126 | 130.6699 | 133.2314 | 140.0668 | 148.0954 | 158.163 | 168.9996 | 177.5597

## Slide 28
EPA’s modeled resource portfolio cannot keep the lights on.
Our modeling found severe capacity shortfalls (rolling blackouts) in MISO when conducting hourly reliability assessments based on historic hourly electricity demand and hourly wind and solar capacity factors.
EPA’s Modeled Grid Would Result in Blackouts

## Slide 29
Conclusion for Mid-West Members!
Hydro power…increasingly valuable
WAPA increasingly valuable
Claire’s personal suggestion
  Make every effort to strengthen your public power relationships
  Identify ways to strengthen the WAPA business enterprise
  Help WAPA strengthen is transmission network!
  Help WAPA maintain and build new transmission assets
  “A successful enterprise needs to build and grow”